## Sheet1
IDX | REG_ADDR | PARAM_NUM | PARAM_NAME | DEF_VAL | MULTIPLIER | NUM_BASE | UNITS
0 | 256 | A1-00 | LANGUAGE SELECTION | 0 | 1 | 10
1 | 257 | A1-01 | ACCESS LEVEL | 2 | 1 | 10
2 | 258 | A1-02 | CONTROL METHOD | 0 | 1 | 10
3 | 259 | A1-03 | INITIALIZE PARAMETERS | 0 | 1 | 10
4 | 260 | A1-04 | ENTER PASSWORD | 0 | 1 | 10
5 | 261 | A1-05 | SELECT PASSWORD | 0 | 1 | 10
6 | 295 | A1-06 | SELECT APPLICATION | 0 | 1 | 10
7 | 296 | A1-07 | DWEZ FUNCTION SELECTION | 1 | 1 | 10
8 | 262 | A2-01 | USER PARAMETER 1 | 258 | 1 | 16
9 | 263 | A2-02 | USER PARAMETER 2 | 384 | 1 | 16
10 | 264 | A2-03 | USER PARAMETER 3 | 385 | 1 | 16
11 | 265 | A2-04 | USER PARAMETER 4 | 386 | 1 | 16
12 | 266 | A2-05 | USER PARAMETER 5 | 512 | 1 | 16
13 | 267 | A2-06 | USER PARAMETER 6 | 513 | 1 | 16
14 | 268 | A2-07 | USER PARAMETER 7 | 547 | 1 | 16
15 | 269 | A2-08 | USER PARAMETER 8 | 548 | 1 | 16
16 | 270 | A2-09 | USER PARAMETER 9 | 640 | 1 | 16
17 | 271 | A2-10 | USER PARAMETER 10 | 641 | 1 | 16
18 | 272 | A2-11 | USER PARAMETER 11 | 642 | 1 | 16
19 | 273 | A2-12 | USER PARAMETER 12 | 643 | 1 | 16
20 | 274 | A2-13 | USER PARAMETER 13 | 658 | 1 | 16
21 | 275 | A2-14 | USER PARAMETER 14 | 768 | 1 | 16
22 | 276 | A2-15 | USER PARAMETER 15 | 770 | 1 | 16
23 | 277 | A2-16 | USER PARAMETER 16 | 771 | 1 | 16
24 | 278 | A2-17 | USER PARAMETER 17 | 772 | 1 | 16
25 | 279 | A2-18 | USER PARAMETER 18 | 773 | 1 | 16
26 | 280 | A2-19 | USER PARAMETER 19 | 776 | 1 | 16
27 | 281 | A2-20 | USER PARAMETER 20 | 780 | 1 | 16
28 | 282 | A2-21 | USER PARAMETER 21 | 782 | 1 | 16
29 | 283 | A2-22 | USER PARAMETER 22 | 785 | 1 | 16
30 | 284 | A2-23 | USER PARAMETER 23 | 792 | 1 | 16
31 | 285 | A2-24 | USER PARAMETER 24 | 1054 | 1 | 16
32 | 286 | A2-25 | USER PARAMETER 25 | 1152 | 1 | 16
33 | 287 | A2-26 | USER PARAMETER 26 | 1170 | 1 | 16
34 | 288 | A2-27 | USER PARAMETER 27 | 0 | 1 | 16
35 | 289 | A2-28 | USER PARAMETER 28 | 0 | 1 | 16
36 | 290 | A2-29 | USER PARAMETER 29 | 0 | 1 | 16
37 | 291 | A2-30 | USER PARAMETER 30 | 0 | 1 | 16
38 | 292 | A2-31 | USER PARAMETER 31 | 0 | 1 | 16
39 | 293 | A2-32 | USER PARAMETER 32 | 0 | 1 | 16
40 | 294 | A2-33 | USER PARAMETER AUTOMATIC REGISTRATION FUNCTION | 0 | 1 | 10
41 | 384 | B1-01 | REFERENCE SELECTION | 1 | 1 | 10
42 | 385 | B1-02 | OPERATION METHOD SELECTION | 1 | 1 | 10
43 | 386 | B1-03 | STOPPING METHOD | 0 | 1 | 10
44 | 387 | B1-04 | REVERSE OPERATION | 0 | 1 | 10
45 | 390 | B1-07 | LOCAL/REMOTE RUN SELECTION | 0 | 1 | 10
46 | 391 | B1-08 | RUN COMMAND AT PROGRAMMING | 0 | 1 | 10
47 | 451 | B1-14 | PHASE TURN SELECTION | 0 | 1 | 10
48 | 452 | B1-15 | REFERENCE SELECTION IN LOCAL CASE | 0 | 1 | 10
49 | 453 | B1-16 | OPERATION METHOD SELECTION IN LOCAL CASE | 0 | 1 | 10
50 | 454 | B1-17 | OPERATION PERMISSION WITH POWER ON/OFF | 0 | 1 | 10
51 | 393 | B2-01 | DC INJECTION START FREQUENCY | 5 | 10 | 10 | Hz
52 | 394 | B2-02 | DC INJECTION CURRENT | 50 | 1 | 10 | %
53 | 395 | B2-03 | DC INJECTION TIME AT START | 0 | 100 | 10 | s
54 | 396 | B2-04 | DC INJECTION TIME AT STOP | 50 | 100 | 10 | s
55 | 400 | B2-08 | MAGNETIC FLUX COMPENSATION VALUE | 0 | 1 | 10 | %
56 | 442 | B2-12 | SHORT CIRCUIT BRAKE TIME AT START | 0 | 100 | 10 | s
57 | 443 | B2-13 | SHORT CIRCUIT BRAKE TIME AT STOP | 50 | 100 | 10 | s
58 | 401 | B3-01 | SPEED SEARCH AT START | 0 | 1 | 10
59 | 402 | B3-02 | SPEED SEARCH CURRENT | 120 | 1 | 10
60 | 403 | B3-03 | SPEED SEARCH DECELERATION TIME | 20 | 10 | 10 | s
61 | 405 | B3-05 | SEARCH WAIT TIME | 2 | 10 | 10 | s
62 | 406 | B3-06 | OUTPUT CURRENT | 5 | 10 | 10
63 | 408 | B3-08 | ACR GAIN FOR SPEED SEARCH | 50 | 100 | 10
64 | 410 | B3-10 | SPEED SEARCH DETECTION COMPENSATION GAIN | 105 | 100 | 10
65 | 414 | B3-14 | BIDIRECTIONAL SEARCH SELECTION | 0 | 1 | 10
66 | 496 | B3-17 | RETRY CURRENT LEVEL | 150 | 1 | 10 | %
67 | 497 | B3-18 | RETRY DETECTION TIME | 10 | 100 | 10 | s
68 | 498 | B3-19 | RETRY COUNT | 3 | 1 | 10
69 | 448 | B3-24 | SPEED SEARCH METHOD SELECTION | 0 | 1 | 10
70 | 456 | B3-25 | SPEED SEARCH RETRY INTERVAL TIME | 5 | 10 | 10 | s
71 | 1916 | B3-29 | SPEED SEARCH INDUCED VOLTAGE LEVEL | 10 | 1 | 10 | %
72 | 419 | B4-01 | DELAY-ON TIMER | 0 | 10 | 10 | s
73 | 420 | B4-02 | DELAY-OFF TIMER | 0 | 10 | 10 | s
74 | 421 | B5-01 | PID CONTROL MODE SELECTION | 0 | 1 | 10
75 | 422 | B5-02 | PID P GAIN | 100 | 100 | 10
76 | 423 | B5-03 | PID I TIME | 10 | 10 | 10 | s
77 | 424 | B5-04 | PID I LIMIT | 1000 | 10 | 10 | %
78 | 425 | B5-05 | PID D TIME | 0 | 100 | 10 | s
79 | 426 | B5-06 | PID LIMIT | 1000 | 10 | 10 | %
80 | 427 | B5-07 | PID OFFSET ADJUSTMENT | 0 | 10 | 10 | %
81 | 428 | B5-08 | PID PRIMARY DELAY TIME CONSTANT | 0 | 100 | 10 | s
82 | 429 | B5-09 | OUTPUT LEVEL SELECTION | 0 | 1 | 10
83 | 430 | B5-10 | PID OUTPUT GAIN | 100 | 100 | 10
84 | 431 | B5-11 | PID OUTPUT REVERSE SELECTION | 0 | 1 | 10
85 | 432 | B5-12 | FEED BACK LOSS DETECTION SELECTION | 0 | 1 | 10
86 | 433 | B5-13 | FEED BACK LOSS DETECTION LEVEL | 0 | 1 | 10 | %
87 | 434 | B5-14 | FEED BACK LOSS DETECTION TIME | 10 | 10 | 10 | s
88 | 435 | B5-15 | PID SLEEP FUNCTION START LEVEL | 0 | 10 | 10 | Hz
89 | 436 | B5-16 | PID SLEEP DELAY TIME | 0 | 10 | 10 | s
90 | 437 | B5-17 | PID ACCEL/DECEL TIME | 0 | 1 | 10 | s
91 | 476 | B5-18 | PID SETPOINT SELECTION | 0 | 1 | 10
92 | 477 | B5-19 | PID SETPOINT VALUE | 0 | 100 | 10 | %
93 | 482 | B5-20 | PID SETPOINT SCALING | 1 | 1 | 10
94 | 415 | B5-34 | PID OUTPUT LOWER LIMIT | 0 | 10 | 10 | %
95 | 416 | B5-35 | PID INPUT LIMIT | 10000 | 10 | 10 | %
96 | 417 | B5-36 | PID FEEDBACK HIGH DETECTION LEVEL | 100 | 1 | 10 | %
97 | 418 | B5-37 | PID FEEDBACK HIGH DETECTION TIME | 10 | 10 | 10 | s
98 | 510 | B5-38 | PID SETPOINT / USER DISPLAY | 10000 | 1 | 10
99 | 511 | B5-39 | PID SETPOINT DISPLAY DIGITS | 2 | 1 | 10
100 | 383 | B5-40 | PID FREF MONITOR SELECTION | 0 | 1 | 10
101 | 381 | B5-47 | PID OUTPUT REVERSE SELECTION2 | 1 | 1 | 10
102 | 438 | B6-01 | DWELL FREQUENCY AT START | 0 | 10 | 10 | Hz
103 | 439 | B6-02 | DWELL TIME AT START | 0 | 10 | 10 | s
104 | 440 | B6-03 | DWELL FREQUENCY AT STOP | 0 | 10 | 10 | Hz
105 | 441 | B6-04 | DWELL TIME AT STOP | 0 | 10 | 10 | s
106 | 460 | B8-01 | ENERGY-SAVING MODE SELECTION | 0 | 1 | 10
107 | 461 | B8-02 | ENERGY SAVING GAIN | 0 | 1 | 10
108 | 462 | B8-03 | ENERGY SAVING CONTROL FILTER TIME CONSTANT | 0 | 1 | 10
109 | 463 | B8-04 | ENERGY-SAVING COEFFICIENT | 1568 | 10 | 10
110 | 464 | B8-05 | KW FILTER TIME | 20 | 1 | 10 | ms
111 | 465 | B8-06 | SEARCH V LIMIT | 0 | 1 | 10 | %
112 | 512 | C1-01 | ACCELERATION TIME 1 | 100 | 10 | 10 | s
113 | 513 | C1-02 | DECELERATION TIME 1 | 100 | 10 | 10 | s
114 | 514 | C1-03 | ACCELERATION TIME 2 | 100 | 10 | 10 | s
115 | 515 | C1-04 | DECELERATION TIME 2 | 100 | 10 | 10 | s
116 | 516 | C1-05 | ACCELERATION TIME 3 FOR MOTOR2 | 100 | 10 | 10 | s
117 | 517 | C1-06 | DECELERATION TIME 3 FOR MOTOR2 | 100 | 10 | 10 | s
118 | 518 | C1-07 | ACCELERATION TIME 4 FOR MOTOR2 | 100 | 10 | 10 | s
119 | 519 | C1-08 | DECELERATION TIME 4 FOR MOTOR2 | 100 | 10 | 10 | s
120 | 520 | C1-09 | EMERGENCY STOP TIME | 100 | 10 | 10 | s
121 | 521 | C1-10 | ACCEL/DECEL TIME SETTING UNIT | 1 | 1 | 10 | s
122 | 522 | C1-11 | ACCEL/DECEL SWITCHING FREQUENCY | 0 | 10 | 10 | Hz
123 | 612 | C1-14 | PICKING UP SPEED AND SLOWING DOWN RATE SETTING STANDARD FREQUENCY | 0 | 10 | 10 | Hz
124 | 523 | C2-01 | S-CURVE ACCELERATION AT START | 20 | 100 | 10 | s
125 | 524 | C2-02 | S-CURVE ACCELERATION AT END | 20 | 100 | 10 | s
126 | 525 | C2-03 | S-CURVE DECELERATION AT START | 20 | 100 | 10 | s
127 | 526 | C2-04 | S-CURVE DECELERATION AT END | 0 | 100 | 10 | s
128 | 527 | C3-01 | SLIP COMPENSATION GAIN | 0 | 10 | 10
129 | 528 | C3-02 | SLIP COMPENSATION TIME | 2000 | 1 | 10 | ms
130 | 529 | C3-03 | SLIP COMPENSATION LIMIT | 200 | 1 | 10 | %
131 | 530 | C3-04 | SLIP COMPENSATION REGENERATION | 0 | 1 | 10
132 | 531 | C3-05 | OUTPUT VOLTAGE LIMIT OPERATION SELECTION | 0 | 1 | 10
133 | 533 | C4-01 | TORQUE COMPENSATION GAIN | 100 | 100 | 10
134 | 534 | C4-02 | TORQUE COMPENSATION PRIMARY DELAY TIME | 200 | 1 | 10 | ms
135 | 535 | C4-03 | TORQUE COMPENSATION AT FORWARD START | 0 | 1 | 10 | %
136 | 536 | C4-04 | TORQUE COMPENSATION AT REVERSE START | 0 | 1 | 10 | %
137 | 537 | C4-05 | TORQUE COMPENSATION TIME CONSTANT | 10 | 1 | 10 | ms
138 | 538 | C4-06 | TORQUE COMPENSATION PRIMARY DELAY TIME 2 | 150 | 1 | 10 | ms
139 | 539 | C5-01 | ASR PROPORTIONAL GAIN 1 | 0 | 1 | 10
140 | 540 | C5-02 | ASR INTEGRAL TIME 1 | 0 | 1 | 10
141 | 541 | C5-03 | AS PROPORTIONAL GAIN 2 | 0 | 1 | 10
142 | 542 | C5-04 | ASR INTEGRAL TIME 2 | 0 | 1 | 10 | s
143 | 543 | C5-05 | ASR LIMIT | 50 | 1 | 10 | %
144 | 547 | C6-01 | DRIVE DUTY SELECTION | 1 | 1 | 10
145 | 548 | C6-02 | CARRIER FREQUENCY SELECTION | 7 | 1 | 10
146 | 549 | C6-03 | CARRIER FREQUENCY UPPER LIMIT | 20 | 1 | 10 | kHz
147 | 550 | C6-04 | CARRIER FREQUENCY LOWER LIMIT | 20 | 1 | 10 | kHz
148 | 551 | C6-05 | CARRIER FREQUENCY PROPORTIONAL GAIN | 0 | 1 | 10
149 | 640 | D1-01 | FREQUENCY REFERENCE 1 | 0 | 100 | 10 | Hz
150 | 641 | D1-02 | FREQUENCY REFERENCE 2 | 0 | 100 | 10 | Hz
151 | 642 | D1-03 | FREQUENCY REFERENCE 3 | 0 | 100 | 10 | Hz
152 | 643 | D1-04 | FREQUENCY REFERENCE 4 | 0 | 100 | 10 | Hz
153 | 644 | D1-05 | FREQUENCY REFERENCE 5 | 0 | 100 | 10 | Hz
154 | 645 | D1-06 | FREQUENCY REFERENCE 6 | 0 | 100 | 10 | Hz
155 | 646 | D1-07 | FREQUENCY REFERENCE 7 | 0 | 100 | 10 | Hz
156 | 647 | D1-08 | FREQUENCY REFERENCE 8 | 0 | 100 | 10 | Hz
157 | 648 | D1-09 | FREQUENCY REFERENCE 9 | 0 | 100 | 10 | Hz
158 | 651 | D1-10 | FREQUENCY REFERENCE 10 | 0 | 100 | 10 | Hz
159 | 652 | D1-11 | FREQUENCY REFERENCE 11 | 0 | 100 | 10 | Hz
160 | 653 | D1-12 | FREQUENCY REFERENCE 12 | 0 | 100 | 10 | Hz
161 | 654 | D1-13 | FREQUENCY REFERENCE 13 | 0 | 100 | 10 | Hz
162 | 655 | D1-14 | FREQUENCY REFERENCE 14 | 0 | 100 | 10 | Hz
163 | 656 | D1-15 | FREQUENCY REFERENCE 15 | 0 | 100 | 10 | Hz
164 | 657 | D1-16 | FREQUENCY REFERENCE 16 | 0 | 100 | 10 | Hz
165 | 658 | D1-17 | JOG FREQUENCY REFERENCE | 600 | 100 | 10 | Hz
166 | 649 | D2-01 | FREQUENCY REFERENCE UPPER LIMIT | 1000 | 10 | 10 | %
167 | 650 | D2-02 | FREQUENCY REFERENCE LOWER LIMIT | 0 | 10 | 10 | %
168 | 659 | D2-03 | MASTER SPEED REFERENCE LOWER LIMIT | 0 | 10 | 10 | %
169 | 660 | D3-01 | JUMP FREQUENCY 1 | 0 | 10 | 10 | Hz
170 | 661 | D3-02 | JUMP FREQUENCY 2 | 0 | 10 | 10 | Hz
171 | 662 | D3-03 | JUMP FREQUENCY 3 | 0 | 10 | 10 | Hz
172 | 663 | D3-04 | JUMP FREQUENCY WIDTH | 10 | 10 | 10 | Hz
173 | 664 | D4-01 | MOP REFERENCE MEMORY | 0 | 1 | 10
174 | 682 | D4-03 | FREQUENCY REFERENCE BIAS STEPS(UP/DOWN2) | 0 | 100 | 10 | Hz
175 | 683 | D4-04 | ACCEL/DECEL RATE SELECTION(UP/DOWN2) | 0 | 1 | 10
176 | 684 | D4-05 | BIAS MODE SELECTION(UP/DOWN2) | 0 | 1 | 10
177 | 685 | D4-06 | BIAS VALUE(UP/DOWN2) | 0 | 10 | 10 | %
178 | 686 | D4-07 | ANALOG CHANGE LIMIT | 10 | 10 | 10 | %
179 | 687 | D4-08 | FREQUENCY REFERENCE BIAS UPPER LIMIT (UP/DOWN2) | 1000 | 10 | 10 | %
180 | 688 | D4-09 | FREQUENCY REFERENCE BIAS LOWER LIMIT (UP/DOWN2) | 0 | 10 | 10 | %
181 | 694 | D4-10 | UP/DOWN FREQUENCY REFERENCE LIMIT SELECTION | 0 | 1 | 10
182 | 690 | D7-01 | OFFSET FREQUENCY 1 | 0 | 10 | 10 | %
183 | 691 | D7-02 | OFFSET FREQUENCY 2 | 0 | 10 | 10 | %
184 | 692 | D7-03 | OFFSET FREQUENCY 3 | 0 | 10 | 10 | %
185 | 768 | E1-01 | INPUT VOLTAGE SETTING | 230 | 1 | 10 | V
186 | 770 | E1-03 | V/F PATTERN SELECTION | 15 | 1 | 10
187 | 771 | E1-04 | MAX. OUTPUT FREQUENCY | 600 | 10 | 10 | Hz
188 | 772 | E1-05 | MAX. VOLTAGE | 2300 | 10 | 10 | V
189 | 773 | E1-06 | BASE FREQUENCY | 600 | 10 | 10 | Hz
190 | 774 | E1-07 | MID OUTPUT FREQUENCY | 30 | 10 | 10 | Hz
191 | 775 | E1-08 | MID OUTPUT FREQUENCY VOLTAGE | 184 | 10 | 10 | V
192 | 776 | E1-09 | MIN. OUTPUT FREQUENCY | 15 | 10 | 10 | Hz
193 | 777 | E1-10 | MIN. OUTPUT FREQUENCY VOLTAGE | 138 | 10 | 10 | V
194 | 778 | E1-11 | MID OUTPUT FREQUENCY 2 | 0 | 10 | 10 | Hz
195 | 779 | E1-12 | MID OUTPUT FREQUENCY VOLTAGE 2 | 0 | 10 | 10 | V
196 | 780 | E1-13 | BASE VOLTAGE | 0 | 10 | 10 | V
197 | 782 | E2-01 | MOTOR RATED CURRENT | 850 | 100 | 10 | A
198 | 783 | E2-02 | MOTOR RATED SLIP | 290 | 100 | 10
199 | 784 | E2-03 | MOTOR NO-LOAD CURRENT | 300 | 100 | 10 | A
200 | 785 | E2-04 | NUMBER OF MOTOR POLES | 4 | 1 | 10
201 | 786 | E2-05 | MOTOR LINE-TO-LINE RESISTANCE | 1601 | 1000 | 10 | Ω
202 | 787 | E2-06 | MOTOR LEAK INDUCTANCE | 184 | 10 | 10 | %
203 | 788 | E2-07 | MOTOR IRON-CORE SATURATION COEFFICIENT 1 | 50 | 100 | 10
204 | 789 | E2-08 | MOTOR IRON-CORE SATURATION COEFFICIENT 2 | 75 | 100 | 10
205 | 790 | E2-09 | MOTOR MECHANICAL LOSS | 0 | 10 | 10 | %
206 | 791 | E2-10 | TORQUE COMPENSATION IRON LOSS COMPENSATION | 77 | 1 | 10 | W
207 | 792 | E2-11 | MOTOR RATED OUTPUT | 220 | 100 | 10 | kW
208 | 808 | E2-12 | MOTOR IRON-CORE SATURATION COEFFICIENT 3 | 130 | 100 | 10
209 | 793 | E3-01 | MOTOR 2 CONTROL METHOD | 0 | 1 | 10
210 | 794 | E3-04 | MOTOR 2 MAX. OUTPUT FREQUENCY | 600 | 10 | 10 | Hz
211 | 795 | E3-05 | MOTOR 2 MAX. VOLTAGE | 2300 | 10 | 10 | V
212 | 796 | E3-06 | MOTOR 2 BASE FREQUENCY | 600 | 10 | 10 | Hz
213 | 797 | E3-07 | MOTOR 2 MID OUTPUT FREQUENCY | 30 | 10 | 10 | Hz
214 | 798 | E3-08 | MOTOR 2 MID OUTPUT FREQUENCY VOLTAGE | 184 | 10 | 10 | V
215 | 799 | E3-09 | MOTOR 2 MIN. OUTPUT FREQUENCY | 15 | 10 | 10 | Hz
216 | 800 | E3-10 | MOTOR 2 MIN. OUTPUT FREQUENCY VOLTAGE | 138 | 10 | 10 | V
217 | 837 | E3-11 | MOTOR 2 MID OUTPUT FREQUENCY 2 | 0 | 10 | 10 | Hz
218 | 838 | E3-12 | MOTOR 2 MID OUTPUT FREQUENCY VOLTAGE 2 | 0 | 10 | 10 | V
219 | 839 | E3-13 | MOTOR 2 BASE VOLTAGE | 0 | 10 | 10 | V
220 | 801 | E4-01 | MOTOR 2 MOTOR RATED CURRENT | 850 | 100 | 10 | A
221 | 802 | E4-02 | MOTOR 2 MOTOR RATED SLIP | 290 | 100 | 10
222 | 803 | E4-03 | MOTOR 2 MOTOR NO-LOAD CURRENT | 300 | 100 | 10 | A
223 | 804 | E4-04 | MOTOR 2 NUMBER OF MOTOR POLES | 4 | 1 | 10
224 | 805 | E4-05 | MOTOR 2 LINE-TO-LINE RESISTANCE | 1601 | 1000 | 10 | Ω
225 | 806 | E4-06 | MOTOR 2 LEAK INDUCTANCE | 184 | 10 | 10 | %
226 | 835 | E4-07 | MOTOR 2 IRON-CORE SATURATION COEFFICIENT 1 | 50 | 100 | 10
227 | 836 | E4-08 | MOTOR 2 IRON-CORE SATURATION COEFFICIENT 2 | 75 | 100 | 10 | kW
228 | 831 | E4-09 | MOTOR 2 MOTOR MECHANICAL LOSS | 0 | 100 | 10
229 | 832 | E4-10 | MOTOR 2 TORQUE COMPENSATION IRON LOSS COMPENSATION | 77 | 1 | 10 | W
230 | 807 | E4-11 | MOTOR 2 RATED CAPACITY | 220 | 100 | 10 | kW
231 | 834 | E4-12 | MOTOR 2 IRON-CORE SATURATION COEFFICIENT 3 | 130 | 100 | 10
232 | 833 | E4-14 | MOTOR 2 SLIP COMPENSATION GAIN | 100 | 10 | 10
233 | 833 | E4-15 | MOTOR 2 TORQUE COMPENSATION GAIN | 100 | 100 | 10
234 | 897 | F1-02 | OPERATION SELECTION AT PG OPEN CIRCUIT | 1 | 1 | 10
235 | 898 | F1-03 | OPERATION SELECTION AT OVERSPEED | 1 | 1 | 10
236 | 899 | F1-04 | OPERATION SELECTION AT DEVIATION | 3 | 1 | 10
237 | 903 | F1-08 | OVERSPEED DETECTION LEVEL | 115 | 1 | 10 | %
238 | 904 | F1-09 | OVERSPEED DETECTION DELAY TIME | 0 | 10 | 10 | s
239 | 905 | F1-10 | EXCESSIVE SPEED DEVIATION DETECTION LEVEL | 10 | 1 | 10 | %
240 | 906 | F1-11 | EXCEESIVE SPEED DEVIATION DETECTION DELAY TIME | 5 | 10 | 10 | s
241 | 909 | F1-14 | PG OPEN-CIRCUIT DETECTION TIME | 20 | 10 | 10 | s
242 | 930 | F6-01 | OPERATION SELECTION AFTER COMMUNICATIONS ERROR | 1 | 1 | 10
243 | 931 | F6-02 | SELECTION OF EXTERNAL FAULT FROM COMMUNICATION OPTION BOARD | 0 | 1 | 10
244 | 932 | F6-03 | STOPPING METHOD FOR EXTERNAL FAULT FROM COMMUNICATION OPTION BOARD | 1 | 1 | 10
245 | 933 | F6-04 | BUS ERROR DETECTION DELAY | 20 | 10 | 10 | s
246 | 936 | F6-07 | FREF PRIORITY SELECTION | 1 | 1 | 10
247 | 874 | F6-08 | COMM PARAMETER INITIALIZE SELECTION | 0 | 1 | 10
248 | 998 | F6-10 | NODE ADDRESS | 168 | 1 | 10
249 | 999 | F6-11 | COMMUNICATION SPEED | 1 | 1 | 10
250 | 955 | F6-14 | BUS ERROR AUTO RESET | 0 | 1 | 10
251 | 875 | F6-20 | M-II STATION ADDRESS | 33 | 1 | 10
252 | 876 | F6-21 | M-II FRAME LENGTH | 0 | 1 | 10
253 | 877 | F6-22 | M-II LINK SPEED | 0 | 1 | 10
254 | 878 | F6-23 | M-II MON E REGISTER | 0 | 1 | 10
255 | 879 | F6-24 | M-II MON F REGISTER | 0 | 1 | 10
256 | 969 | F6-25 | M-II WDT ERROR SELECTION | 1 | 1 | 10
257 | 970 | F6-26 | M-II NUMBER OF BUS ERROR DETECTION | 2 | 1 | 10
258 | 971 | F6-30 | NODE ADDRESS | 0 | 1 | 10
259 | 972 | F6-31 | CLEAR MODE SELECTION | 0 | 1 | 10
260 | 973 | F6-32 | PROFIBUSMAP SELECTION | 0 | 1 | 10
261 | 976 | F6-35 | CANOPEN NODE ADDRESS | 0 | 1 | 10
262 | 977 | F6-36 | COMMUNICATION SPEED | 6 | 1 | 10
263 | 981 | F6-40 | NODE ADDRESS | 0 | 1 | 10
264 | 982 | F6-41 | COMMUNICATION SPEED | 1 | 1 | 10
265 | 961 | F6-50 | MAC ADDRESS | 64 | 1 | 10
266 | 962 | F6-51 | BAUD RATE | 4 | 1 | 10
267 | 963 | F6-52 | PCA SETTING | 21 | 1 | 10
268 | 964 | F6-53 | PPA SETTING | 71 | 1 | 10
269 | 965 | F6-54 | IDLE MODE FAULT DETECTION | 0 | 1 | 10
270 | 966 | F6-55 | DEVICENET BAUD RATE MONITOR | 0 | 1 | 10
271 | 983 | F6-56 | SPEED SCALING | 0 | 1 | 10
272 | 984 | F6-57 | CURRENT SCALING | 0 | 1 | 10
273 | 985 | F6-58 | TORQUE SCALING | 0 | 1 | 10
274 | 986 | F6-59 | POWER SCALING | 0 | 1 | 10
275 | 987 | F6-60 | VOLTAGE SCALING | 0 | 1 | 10
276 | 988 | F6-61 | TIME SCALING | 0 | 1 | 10
277 | 989 | F6-62 | HEART BEAT | 0 | 1 | 10
278 | 990 | F6-63 | DYNAMIC OUTPUT MAC ID MEMORY | 63 | 1 | 10
279 | 991 | F6-64 | DYNAMIC OUTPUT ASSEMBLY 109 PARAMETER 1 | 0 | 1 | 10
280 | 992 | F6-65 | DYNAMIC OUTPUT ASSEMBLY 109 PARAMETER 2 | 0 | 1 | 10
281 | 993 | F6-66 | DYNAMIC OUTPUT ASSEMBLY 109 PARAMETER 3 | 0 | 1 | 10
282 | 994 | F6-67 | DYNAMIC OUTPUT ASSEMBLY 109 PARAMETER 4 | 0 | 1 | 10
283 | 995 | F6-68 | DYNAMIC INPUT ASSEMBLY 159 PARAMETER 1 | 0 | 1 | 10
284 | 996 | F6-69 | DYNAMIC INPUT ASSEMBLY 159 PARAMETER 2 | 0 | 1 | 10
285 | 967 | F6-70 | DYNAMIC INPUT ASSEMBLY 159 PARAMETER 3 | 0 | 1 | 10
286 | 968 | F6-71 | DYNAMIC INPUT ASSEMBLY 159 PARAMETER 4 | 0 | 1 | 10
287 | 997 | F7-01 | IP ADDRESS1 | 192 | 1 | 10
288 | 998 | F7-02 | IP ADDRESS2 | 168 | 1 | 10
289 | 999 | F7-03 | IP ADDRESS3 | 1 | 1 | 10
290 | 1000 | F7-04 | IP ADDRESS4 | 20 | 1 | 10
291 | 1001 | F7-05 | SUBNET MASK1 | 255 | 1 | 10
292 | 1002 | F7-06 | SUBNET MASK2 | 255 | 1 | 10
293 | 1003 | F7-07 | SUBNET MASK3 | 255 | 1 | 10
294 | 1004 | F7-08 | SUBNET MASK4 | 0 | 1 | 10
295 | 1005 | F7-09 | GATEWAY ADDRESS1 | 192 | 1 | 10
296 | 1006 | F7-10 | GATEWAY ADDRESS2 | 168 | 1 | 10
297 | 1007 | F7-11 | GATEWAY ADDRESS3 | 1 | 1 | 10
298 | 992 | F7-12 | GATEWAY ADDRESS4 | 0 | 1 | 10
299 | 1009 | F7-13 | ADDRESS STARTUP MODE | 2 | 1 | 10
300 | 1010 | F7-14 | DUPLEX MODE SETTING | 1 | 1 | 10
301 | 1011 | F7-15 | SPEED MODE SETTING | 10 | 1 | 10
302 | 1012 | F7-16 | TIMEOUT VALUE | 0 | 1 | 10
303 | 1013 | F7-17 | SPEED SCALING | 0 | 1 | 10
304 | 1014 | F7-18 | CURRENT SCALING | 0 | 1 | 10
305 | 1015 | F7-19 | TORQUE SCALING | 0 | 1 | 10
306 | 1016 | F7-20 | POWER SCALING | 0 | 1 | 10
307 | 1017 | F7-21 | VOLTAGE SCALING | 0 | 1 | 10
308 | 1018 | F7-22 | TIME SCALING | 0 | 1 | 10
309 | 1019 | F7-23 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 1 | 0 | 1 | 10
310 | 1020 | F7-24 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 2 | 0 | 1 | 10
311 | 1021 | F7-25 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 3 | 0 | 1 | 10
312 | 1022 | F7-26 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 4 | 0 | 1 | 10
313 | 1023 | F7-27 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 5 | 0 | 1 | 10
314 | 1024 | F7-28 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 6 | 36 | 1 | 10
315 | 1025 | F7-29 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 7 | 20 | 1 | 10
316 | 1026 | F7-30 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 8 | 3 | 1 | 10
317 | 1027 | F7-31 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 9 | 4 | 1 | 10
318 | 1028 | F7-32 | DYNAMIC OUTPUT ASSEMBLY 116 PARAMETER 10 | 6 | 1 | 10
319 | 1034 | F7-38 | DYNAMIC INPUT ASSEMBLY 166 PARAMETER 6 | 0 | 1 | 10
320 | 1035 | F7-39 | DYNAMIC INPUT ASSEMBLY 166 PARAMETER 7 | 14 | 1 | 10
321 | 1036 | F7-40 | DYNAMIC INPUT ASSEMBLY 166 PARAMETER 8 | 0 | 1 | 10
322 | 1037 | F7-41 | DYNAMIC INPUT ASSEMBLY 166 PARAMETER 9 | 2 | 1 | 10
323 | 1080 | H1-01 | TERMINAL S1 FUNCTION SELECTION | 144 | 1 | 16
324 | 1081 | H1-02 | TERMINAL S2 FUNCTION SELECTION | 145 | 1 | 16
325 | 1024 | H1-03 | TERMINAL S3 FUNCTION SELECTION | 36 | 1 | 16
326 | 1025 | H1-04 | TERMINAL S4 FUNCTION SELECTION | 20 | 1 | 16
327 | 1026 | H1-05 | TERMINAL S5 FUNCTION SELECTION | 3 | 1 | 16
328 | 1027 | H1-06 | TERMINAL S6 FUNCTION SELECTION | 4 | 1 | 16
329 | 1028 | H1-07 | TERMINAL S7 FUNCTION SELECTION | 6 | 1 | 16
330 | 1035 | H2-01 | TERMINAL MA/MB-MC SELECTION | 14 | 1 | 16
331 | 1036 | H2-02 | TERMINAL P1 SELECTION | 0 | 1 | 16
332 | 1037 | H2-03 | TERMINAL P2 SELECTION | 2 | 1 | 16
333 | 1079 | H2-06 | OUTPUT UNIT SELECTION | 0 | 1 | 10
334 | 1040 | H3-01 | TERMINAL A1 SIGNAL LEVEL SELECTION | 0 | 1 | 10
335 | 1076 | H3-02 | TERMINAL A1 FUNCTION SELECTION | 0 | 1 | 10
336 | 1041 | H3-03 | TERMINAL A1 GAIN SETTING | 1000 | 10 | 10 | %
337 | 1042 | H3-04 | TERMINAL A1 BIAS SETTING | 0 | 10 | 10 | %
338 | 1047 | H3-09 | TERMINAL A2 SIGNAL LEVEL SELECTION | 2 | 1 | 10
339 | 1048 | H3-10 | TERMINAL A2 FUNCTION SELECTION | 0 | 1 | 10
340 | 1049 | H3-11 | TERMINAL A2 GAIN SETTING | 1000 | 10 | 10 | %
341 | 1050 | H3-12 | TERMINAL A2 BIAS SETTING | 0 | 10 | 10 | %
342 | 1051 | H3-13 | FILTER AVG TIME | 3 | 100 | 10 | s
343 | 1052 | H3-14 | TERMINAL ANALOG INPUT SELECTION(WHEN H1-XX = C) | 7 | 1 | 10
344 | 1088 | H3-16 | A1 OFFSET | 0 | 1 | 10
345 | 1089 | H3-17 | A2 OFFSET | 0 | 1 | 10
346 | 1053 | H4-01 | MULTI-FUNCTION ANALOG 1(ANALOG TERMINAL MONITOR SELECTION) | 102 | 1 | 10
347 | 1054 | H4-02 | MULTI-FUNCTION ANALOG 1(ANALOG TERMINAL OUTPUT GAIN) | 1000 | 10 | 10 | %
348 | 1055 | H4-03 | MULTI-FUNCTION ANALOG 1(ANALOG TERMINAL OUTPUT BIAS) | 0 | 10 | 10 | %
349 | 1061 | H5-01 | DRIVE NODE ADDRESS | 31 | 1 | 10
350 | 1062 | H5-02 | COMMUNICATION SPEED SELECTION | 3 | 1 | 10
351 | 1063 | H5-03 | COMMUNICATION PARITY SELECTION | 0 | 1 | 10
352 | 1064 | H5-04 | SERIAL FAULT SELECTION | 3 | 1 | 10
353 | 1065 | H5-05 | CE DETECTION SELECTION | 1 | 1 | 10
354 | 1066 | H5-06 | SEND WAIT TIME | 5 | 1 | 10 | ms
355 | 1067 | H5-07 | RTS CONTROL ON/OFF | 1 | 1 | 10
356 | 1077 | H5-09 | CE DETECTION TIME | 20 | 10 | 10 | s
357 | 1078 | H5-10 | OUTPUT VOLTAGE MONITOR(REGISTER NO.25) UNIT | 0 | 1 | 10
358 | 1084 | H5-11 | ENTER FUNCTION SELECTION OF TRANSMISSION | 1 | 1 | 10
359 | 1085 | H5-12 | RUN COMMAND METHOD SELECTION | 0 | 1 | 10
360 | 1068 | H6-01 | PULSE TRAIN INPUT FUNCTION SELECTION | 0 | 1 | 10
361 | 1069 | H6-02 | PULSE TRAIN INPUT SCALING | 1440 | 1 | 10 | Hz
362 | 1070 | H6-03 | PULSE TRAIN INPUT GAIN | 1000 | 10 | 10 | %
363 | 1071 | H6-04 | PULSE TRAIN INPUT BIAS | 0 | 10 | 10 | %
364 | 1072 | H6-05 | PULSE TRAIN INPUT FILTER TIME | 10 | 100 | 10 | s
365 | 1073 | H6-06 | PULSE TRAIN MONITOR SELECTION | 102 | 1 | 10
366 | 1074 | H6-07 | PULSE TRAIN MONITOR SCALING | 1440 | 1 | 10 | Hz
367 | 1152 | L1-01 | MOTOR OVERLOAD PROTECTION | 1 | 1 | 10
368 | 1153 | L1-02 | MOTOR OVERLOAD PROTECTION TIME | 10 | 10 | 10 | min
369 | 1154 | L1-03 | MOTOR OVERHEAT ALARM OPERATION SELECTION | 3 | 1 | 10
370 | 1155 | L1-04 | MOTOR OVERHEAT FAULT OPERATION SELECTION | 1 | 1 | 10
371 | 1156 | L1-05 | MOTOR TEMPERATURE INPUT FILTER TIME | 20 | 100 | 10 | s
372 | 1133 | L1-13 | ELECTROTHERMAL OPERATION SELECTION | 1 | 1 | 10
373 | 1896 | L1-22 | LEAKAGE CURRENT FILTER TIME CONSTANT 1 | 0 | 10 | 10 | s
374 | 1897 | L1-23 | LEAKAGE CURRENT FILTER TIME CONSTANT 2 | 0 | 10 | 10 | s
375 | 1157 | L2-01 | MOMENTARY POWER LOSS DETECTION | 0 | 1 | 10
376 | 1158 | L2-02 | MOMENTARY POWER LOSS RIDETHRU TIME | 3 | 10 | 10 | s
377 | 1159 | L2-03 | MIN. BASEBLOCK TIME | 5 | 10 | 10 | s
378 | 1160 | L2-04 | VOLTAGE RECOVERY TIME | 3 | 10 | 10 | s
379 | 1161 | L2-05 | UNDERVOLTAGE DETECTION LEVEL | 190 | 1 | 10 | V
380 | 1162 | L2-06 | KEB DECELERATION TIME | 0 | 10 | 10 | s
381 | 1163 | L2-07 | KEB ACCELERATION TIME | 0 | 10 | 10 | s
382 | 1164 | L2-08 | KEB START OUTPUT FREQUENCY REDUCTION | 100 | 1 | 10 | %
383 | 1121 | L2-11 | DESIRED DC BUS VOLTAGE DURING KEB | 240 | 1 | 10 | V
384 | 1167 | L3-01 | STALL PREVENTION ACCELERATION SELECTION | 1 | 1 | 10
385 | 1168 | L3-02 | STALL PREVENTION ACCELERATION LEVEL | 120 | 1 | 10 | %
386 | 1169 | L3-03 | STALL PREVENTION LIMIT DURING ACCELERATION | 50 | 1 | 10 | %
387 | 1170 | L3-04 | STALL PREVENTION DECELERATION SELECTION | 1 | 1 | 10
388 | 1171 | L3-05 | STALL PREVENTION RUNNING SELECTION | 1 | 1 | 10
389 | 1172 | L3-06 | STALL PREVENTION RUNNING LEVEL | 120 | 1 | 10 | %
390 | 1223 | L3-11 | OV SUPPRESSION FUNCTION SELECTION | 0 | 1 | 10
391 | 1122 | L3-17 | OV SUPPRESSION, DECEL STALL, AND BUS VOLTAGE DURING STALL | 370 | 1 | 10 | V
392 | 1125 | L3-20 | ADJUSTMENT GAIN | 100 | 100 | 10
393 | 1126 | L3-21 | DECELERATION RATE OPERATION GAIN | 100 | 100 | 10
394 | 1273 | L3-22 | DECELERATION TIME AT STALL PREVENTION DURING ACCELERATION | 0 | 1 | 10
395 | 1277 | L3-23 | STALLP RUNNING LEVEL OUTPUT AUTO REDUCTION | 0 | 1 | 10
396 | 1134 | L3-24 | INERTIA CONVERSION MOTOR ACCELERATION TIME | 145 | 1000 | 10 | s
397 | 1135 | L3-25 | LOAD INERTIA P | 10 | 10 | 10
398 | 1177 | L4-01 | SPEED AGREEMENT LEVEL | 0 | 10 | 10 | Hz
399 | 1178 | L4-02 | SPEED AGREEMENT WIDTH | 20 | 10 | 10 | Hz
400 | 1179 | L4-03 | SPEED AGREEMENT LEVEL +- | 0 | 10 | 10 | Hz
401 | 1180 | L4-04 | SPEED AGREEMENT WIDTH +- | 20 | 10 | 10 | Hz
402 | 1181 | L4-05 | REFERENCE LOSS SELECTION | 0 | 1 | 10
403 | 1218 | L4-06 | FREQUENCY REFERENCE AT FLOSS | 800 | 10 | 10 | %
404 | 1136 | L4-07 | CONDITIONS OF FREQUENCY DETECTION | 0 | 1 | 10
405 | 1151 | L4-08 | SPEED AGREEMENT DETECTION CONDITIONS | 0 | 1 | 10
406 | 1182 | L5-01 | NUMBER OF AUTO RESTART ATTEMPTS | 0 | 1 | 10
407 | 1183 | L5-02 | AUTO RESTART OPERATION SELECTION | 0 | 1 | 10
408 | 1132 | L5-04 | FAULT RESET INTERVAL TIME | 100 | 10 | 10 | s
409 | 1127 | L5-05 | AUTO RESTART SELECTION | 0 | 1 | 10
410 | 1185 | L6-01 | TORQUE DETECTION SELECTION 1 | 0 | 1 | 10
411 | 1186 | L6-02 | TORQUE DETECTION LEVEL 1 | 150 | 1 | 10 | %
412 | 1187 | L6-03 | TORQUE DETECTION TIME 1 | 1 | 10 | 10 | s
413 | 1188 | L6-04 | TORQUE DETECTION SELECTION 2 | 0 | 1 | 10
414 | 1189 | L6-05 | TORQUE DETECTION LEVEL 2 | 150 | 1 | 10 | %
415 | 1190 | L6-06 | TORQUE DETECTION TIME 2 | 1 | 10 | 10 | s
416 | 1128 | L6-08 | MACHINE DEGRADATION DETECTION SELECTION | 0 | 1 | 10
417 | 1129 | L6-09 | MACHINE DEGRADATION DETECTION SPEED LEVEL | 1100 | 10 | 10 | %
418 | 1130 | L6-10 | MACHINE DEGRADATION DETECTION TIME | 1 | 10 | 10 | s
419 | 1131 | L6-11 | MACHINE DEGRADATION DETECTION START TIME | 0 | 1 | 10
420 | 1191 | L7-01 | FORWARD TORQUE LIMIT | 200 | 1 | 10 | %
421 | 1192 | L7-02 | REVERSE TORQUE LIMIT | 200 | 1 | 10 | %
422 | 1193 | L7-03 | FORWARD REGENERATIVE TORQUE LIMIT | 200 | 1 | 10 | %
423 | 1194 | L7-04 | REVERSE REGENERATIVE TORQUE LIMIT | 200 | 1 | 10 | %
424 | 1196 | L7-06 | TORQUE LIMIT INTEGRAL TIME CONSTANT | 200 | 1 | 10 | ms
425 | 1225 | L7-07 | TORQUE LIMIT CONTROL METHOD SELECTION DURING ACCEL/DECEL | 0 | 1 | 10
426 | 1197 | L8-01 | DB RESISTOR PROTECT | 0 | 1 | 10
427 | 1198 | L8-02 | OVERHEAT PRE-ALARM LEVEL | 100 | 1 | 10 | °C
428 | 1199 | L8-03 | OVERHEAT PRE-ALARM SELECTION | 3 | 1 | 10
429 | 1201 | L8-05 | PHASE LOSS INPUT SELECTION | 1 | 1 | 10
430 | 1203 | L8-07 | PHASE LOSS OUTPUT SELECTION | 1 | 1 | 10
431 | 1205 | L8-09 | GROUND PROTECTION SELECTION | 0 | 1 | 10
432 | 1206 | L8-10 | COOLING FAN CONTROL SELECTION | 0 | 1 | 10
433 | 1207 | L8-11 | COOLING FAN CONTROL DELAY TIME | 60 | 1 | 10 | s
434 | 1208 | L8-12 | AMBIENT TEMPERATURE | 40 | 1 | 10 | °C
435 | 1211 | L8-15 | OL CHARACTERISTICS AT LOW SPEEDS | 1 | 1 | 10
436 | 1214 | L8-18 | SOFTWARE CLA SELECTION | 1 | 1 | 10
437 | 1215 | L8-19 | FREQUENCY REDUCTION RATE DURING OH PRE-ALARM | 8 | 10 | 10
438 | 1247 | L8-29 | CURRENT UNABALANCE DETECTION | 1 | 1 | 10
439 | 1260 | L8-35 | INSTALLATION METHOD SELECTION | 0 | 1 | 10
440 | 1263 | L8-38 | CARRIER FREQUENCY DECEL SELECTION | 1 | 1 | 10
441 | 1265 | L8-40 | REDUCTION CARRIER FREQUENCY TIME | 50 | 100 | 10 | s
442 | 1266 | L8-41 | CURRENT WARNING | 0 | 1 | 10
443 | 1137 | L8-51 | STO FAULT DETECTION LEVEL | 0 | 1 | 10 | %
444 | 1140 | L8-54 | STO DEVIATION DETECTION | 1 | 1 | 10
445 | 1408 | N1-01 | HUNTING-PREVENTION SELECTION | 1 | 1 | 10
446 | 1409 | N1-02 | HUNTING-PREVENTION GAIN | 100 | 100 | 10
447 | 1410 | N1-03 | HUNTING-PREVENTION TIME | 10 | 1 | 10 | ms
448 | 1328 | N1-05 | REVERSE HUNTING PREV GAIN | 0 | 100 | 10
449 | 1412 | N2-01 | AFR GAIN | 100 | 1 | 10
450 | 1413 | N2-02 | AFR TIME CONSTANT | 50 | 1 | 10 | ms
451 | 1414 | N2-03 | AFR TIME CONSTANT 2 | 750 | 1 | 10 | ms
452 | 1416 | N3-01 | HSB DECELERATION FREQUENCY WIDTH | 5 | 1 | 10 | %
453 | 1417 | N3-02 | HSB CURRENT | 150 | 1 | 10 | %
454 | 1418 | N3-03 | HSB DWELL TIME | 10 | 10 | 10 | s
455 | 1419 | N3-04 | HSB OL TIME | 40 | 1 | 10 | s
456 | 1329 | N3-13 | OVER EXCITING DECELERATION GAIN | 110 | 100 | 10
457 | 1401 | N3-21 | OVER SLIP INHIBIT CURRENT LEVEL | 100 | 1 | 10 | %
458 | 1403 | N3-23 | OVER EXCITATION RUN | 0 | 1 | 10
459 | 1392 | N6-01 | LINE-TO-LINE MOTOR RESISTANCE ONLINE TUNING | 1 | 1 | 10
460 | 1336 | N8-45 | SPEED FEEDBACK DETECTION CONTORL GAIN | 80 | 1 | 10
461 | 1338 | N8-47 | PULL-IN CURRENT COMPENSATION TIME CONSTANT | 50 | 1 | 10 | s
462 | 1339 | N8-48 | PULL-IN CURRENT COMPENSATION TIME CONSTANT | 30 | 1 | 10 | %
463 | 1340 | N8-49 | D-AXIS CURRENT FOR HIGH EFFICIENCY CONTROL | 0 | 1 | 10 | %
464 | 1342 | N8-51 | ACCELERATION PULL-IN CURRENT | 50 | 1 | 10 | %
465 | 1389 | N8-54 | VOLTAGE ERROR COMPENSATION TIME CONSTANT | 100 | 1 | 10 | s
466 | 1390 | N8-55 | LOAD INERTIA | 0 | 1 | 10
467 | 1405 | N8-62 | OUTPUT VOLTAGE HIGH LIMIT | 2000 | 1 | 10 | VAC
468 | 1406 | N8-63 | OUTPUT VOLTAGE LIMIT GAIN | 100 | 1 | 10
469 | 1628 | N8-65 | SPEED FEEDBACK DETECTION CONTROL GAIN DURING OV SUPPRESSION | 150 | 1 | 10
470 | 567 | N8-68 | OUTPUT VOLTAGE LIMIT GAIN 2 | 95 | 1 | 10
471 | 700 | N8-87 | OUTPUT VOLTAGE LIMIT SELECTION | 0 | 1 | 10
472 | 701 | N8-88 | OUTPUT VOLTAGE LIMIT SWITCHING CURRENT LEVEL | 400 | 1 | 10 | %
473 | 702 | N8-89 | OUTPUT VOLTAGE LIMIT SWITCHING CURRENT HYSTERESIS WIDTH | 3 | 1 | 10 | %
474 | 703 | N8-90 | OUTPUT VOLTAGE LIMIT SWITCHING SPEED | 200 | 1 | 10 | %
475 | 759 | N8-91 | ID LIMIT FOR OUTPUT VOLTAGE LIMIT CONTROL | 65486 | 1 | 10 | %
476 | 1280 | O1-01 | MONITOR SELECTION | 106 | 1 | 10
477 | 1281 | O1-02 | MONITOR SELECTION AFTER POWER UP | 1 | 1 | 10
478 | 1282 | O1-03 | DISPLAY SCALING | 0 | 1 | 10
479 | 1284 | O1-05 | LCD CONTRAST | 3 | 1 | 10
480 | 1313 | O1-11 | FREQUENCY REFERENCE SETTING / DECIMAL DISPLAY | 2 | 1 | 10
481 | 1285 | O2-01 | LOCAL/REMOTE KEY ENABLE/DISABLE | 1 | 1 | 10
482 | 1286 | O2-02 | OPERATION STOP KEY | 1 | 1 | 10
483 | 1287 | O2-03 | USER PARAMETER DEFAULT VALUE | 0 | 1 | 10
484 | 1288 | O2-04 | KVA SELECTION | 101 | 1 | 10
485 | 1289 | O2-05 | FREQUENCY REFERENCE SETTING METHOD SELECTION | 0 | 1 | 10
486 | 1290 | O2-06 | OPERATOR DETECTION | 0 | 1 | 10
487 | 1319 | O2-07 | BIDIRECTIONAL WHEN THE INVERTER POWER IS ON | 0 | 1 | 10
488 | 1301 | O3-01 | COPY FUNCTOIN SELECTION | 0 | 1 | 10
489 | 1302 | O3-02 | COPY ALLOWED SELECTION | 0 | 1 | 10
490 | 1291 | O4-01 | ACCUMULATED OPERATION TIME SETTING | 0 | 1 | 10
491 | 1292 | O4-02 | ACCUMULATED OPERATION TIME SELECTION | 0 | 1 | 10
492 | 1294 | O4-03 | COOLING FAN OPERATION TIME SETTING | 0 | 1 | 10
493 | 1309 | O4-05 | CAPACITOR MAINTENANCE SETTING | 0 | 1 | 10 | %
494 | 1315 | O4-07 | DC BUS PRE-CHARGE RELAY MAINTENANCE SETTING | 0 | 1 | 10 | %
495 | 1317 | O4-09 | IGBT MAINTENANCE SETTING | 0 | 1 | 10 | %
496 | 1296 | O4-11 | U2, U3 INITIALIZATION | 0 | 1 | 10
497 | 1298 | O4-12 | KWH MONITOR INITIALIZATION | 0 | 1 | 10
498 | 1320 | O4-13 | NUMBER OF RUN COMMANDS INITIALIZE SELECTION | 0 | 1 | 10
499 | 5632 | Q1-01 | CUSTOM PARAMETER 1 | 0 | 100 | 10 | %
500 | 5633 | Q1-02 | CUSTOM PARAMETER 2 | 0 | 100 | 10 | %
501 | 5634 | Q1-03 | CUSTOM PARAMETER 3 | 0 | 100 | 10 | %
502 | 5635 | Q1-04 | CUSTOM PARAMETER 4 | 0 | 100 | 10 | %
503 | 5636 | Q1-05 | CUSTOM PARAMETER 5 | 0 | 100 | 10 | %
504 | 5637 | Q1-06 | CUSTOM PARAMETER 6 | 0 | 100 | 10 | %
505 | 5638 | Q1-07 | CUSTOM PARAMETER 7 | 0 | 10 | 10 | %
506 | 5639 | Q1-08 | CUSTOM PARAMETER 8 | 0 | 10 | 10 | %
507 | 5640 | Q1-09 | CUSTOM PARAMETER 9 | 0 | 10 | 10 | %
508 | 5641 | Q1-10 | CUSTOM PARAMETER 10 | 0 | 1 | 10
509 | 5706 | Q2-11 | DRIVE U1 MONITOR SELECT 1 | 0 | 1 | 10
510 | 5707 | Q2-12 | DRIVE U1 MONITOR SELECT 2 | 0 | 1 | 10
511 | 5760 | Q3-01 | TIMER #1 DELAY | 0 | 10 | 10 | s
512 | 5761 | Q3-02 | TIMER #2 DELAY | 0 | 10 | 10 | s
513 | 5762 | Q3-03 | TIMER #3 DELAY | 0 | 10 | 10 | s
514 | 5763 | Q3-04 | 1 SHOT ON TIME | 0 | 10 | 10 | s
515 | 5764 | Q3-05 | INTERVAL TIMER OFF TIME | 0 | 10 | 10 | s
516 | 5765 | Q3-06 | INTERVAL TIMER ON TIME | 0 | 10 | 10 | s
517 | 5824 | Q4-01 | RAMP TIME | 0 | 10 | 10 | s
518 | 5825 | Q4-02 | DELAY FILTER TIME | 5 | 10 | 10 | s
519 | 5826 | Q4-03 | SCALE #1 MULTIPLIER | 1 | 1 | 10
520 | 5827 | Q4-04 | SCALE #1 DIVISOR | 1 | 1 | 10
521 | 5828 | Q4-05 | SCALE #1 BIAS | 0 | 100 | 10
522 | 5829 | Q4-06 | UPPER LIMIT 1 | 0 | 100 | 10 | %
523 | 5830 | Q4-07 | LOWER LIMIT 1 | 0 | 100 | 10 | %
524 | 5831 | Q4-08 | UPPER LIMIT 2 | 0 | 100 | 10 | %
525 | 5832 | Q4-09 | LOWER LIMIT 2 | 0 | 100 | 10 | %
526 | 5833 | Q4-10 | DEAD ZONE | 0 | 100 | 10 | %
527 | 5834 | Q4-11 | LIMIT/DEAD ZONE PROPERTIES | 0 | 1 | 10
528 | 5835 | Q4-12 | SCALE #2 MULTIPLIER | 1 | 1 | 10
529 | 5836 | Q4-13 | SCALE #2 DIVISOR | 1 | 1 | 10
530 | 5837 | Q4-14 | SCALE #2 BIAS | 0 | 100 | 10
531 | 5888 | Q5-01 | MOP TIME | 0 | 10 | 10 | %
532 | 5889 | Q5-02 | MOP MIN VALUE | 0 | 10 | 10 | %
533 | 5890 | Q5-03 | MOP MAX VALUE | 0 | 10 | 10 | %
534 | 5891 | Q5-04 | MOP RESET VALUE | 0 | 10 | 10 | %
535 | 5892 | Q5-05 | STEP MOP AMOUNT | 0 | 10 | 10 | %
536 | 5893 | Q5-06 | STEP MOP MIN VALUE | 0 | 10 | 10 | %
537 | 5894 | Q5-07 | STEP MOP MAX VALUE | 0 | 10 | 10 | %
538 | 5895 | Q5-08 | STEP MOP RESET VALUE | 0 | 10 | 10 | %
539 | 5896 | Q5-09 | COMPARE <= HYSTERESIS LEVEL | 0 | 100 | 10 | %
540 | 5897 | Q5-10 | COMPARE = BANDWIDTH | 0 | 100 | 10 | %
541 | 5898 | Q5-11 | COMPARE >= HYSTERESIS LEVEL | 0 | 100 | 10 | %
542 | 5952 | Q6-01 | PI PROPERTIES | 0 | 1 | 10
543 | 5953 | Q6-02 | PI LOG INPUT SEL | 16 | 1 | 10
544 | 5954 | Q6-03 | PI PROP GAIN | 100 | 100 | 10
545 | 5955 | Q6-04 | PI INT TIME | 10 | 10 | 10 | s
546 | 5956 | Q6-05 | PI INT LIMIT | 1000 | 10 | 10 | %
547 | 5957 | Q6-06 | PI LIMIT | 1000 | 10 | 10 | %
548 | 5958 | Q6-07 | PI OUTPUT GAIN | 100 | 100 | 10
549 | 6208 | R1-01 | PARAMETER 1 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 321 | 1 | 16
550 | 6209 | R1-02 | PARAMETER 1 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 113 | 1 | 16
551 | 6210 | R1-03 | PARAMETER 2 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 43 | 1 | 16
552 | 6211 | R1-04 | PARAMETER 2 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
553 | 6212 | R1-05 | PARAMETER 3 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 115 | 1 | 16
554 | 6213 | R1-06 | PARAMETER 3 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 224 | 1 | 16
555 | 6214 | R1-07 | PARAMETER 4 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 322 | 1 | 16
556 | 6215 | R1-08 | PARAMETER 4 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 113 | 1 | 16
557 | 6216 | R1-09 | PARAMETER 5 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 43 | 1 | 16
558 | 6217 | R1-10 | PARAMETER 5 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
559 | 6218 | R1-11 | PARAMETER 6 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 115 | 1 | 16
560 | 6219 | R1-12 | PARAMETER 6 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 225 | 1 | 16
561 | 6220 | R1-13 | PARAMETER 7 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 321 | 1 | 16
562 | 6221 | R1-14 | PARAMETER 7 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 392 | 1 | 16
563 | 6222 | R1-15 | PARAMETER 8 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 393 | 1 | 16
564 | 6223 | R1-16 | PARAMETER 8 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 113 | 1 | 16
565 | 6224 | R1-17 | PARAMETER 9 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 322 | 1 | 16
566 | 6225 | R1-18 | PARAMETER 9 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 392 | 1 | 16
567 | 6226 | R1-19 | PARAMETER 10 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 393 | 1 | 16
568 | 6227 | R1-20 | PARAMETER 10 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
569 | 6228 | R1-21 | PARAMETER 11 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 115 | 1 | 16
570 | 6229 | R1-22 | PARAMETER 11 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 113 | 1 | 16
571 | 6230 | R1-23 | PARAMETER 12 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 47 | 1 | 16
572 | 6231 | R1-24 | PARAMETER 12 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
573 | 6232 | R1-25 | PARAMETER 13 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 115 | 1 | 16
574 | 6233 | R1-26 | PARAMETER 13 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
575 | 6234 | R1-27 | PARAMETER 14 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 26 | 1 | 16
576 | 6235 | R1-28 | PARAMETER 14 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 392 | 1 | 16
577 | 6236 | R1-29 | PARAMETER 15 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 393 | 1 | 16
578 | 6237 | R1-30 | PARAMETER 15 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 113 | 1 | 16
579 | 6238 | R1-31 | PARAMETER 16 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 115 | 1 | 16
580 | 6239 | R1-32 | PARAMETER 16 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 159 | 1 | 16
581 | 6240 | R1-33 | PARAMETER 17 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 162 | 1 | 16
582 | 6241 | R1-34 | PARAMETER 17 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 220 | 1 | 16
583 | 6242 | R1-35 | PARAMETER 18 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 322 | 1 | 16
584 | 6243 | R1-36 | PARAMETER 18 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 392 | 1 | 16
585 | 6244 | R1-37 | PARAMETER 19 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 393 | 1 | 16
586 | 6245 | R1-38 | PARAMETER 19 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 114 | 1 | 16
587 | 6246 | R1-39 | PARAMETER 20 FOR CONNECTING DRIVEWORKSEZ (UPPER) | 321 | 1 | 16
588 | 6247 | R1-40 | PARAMETER 20 FOR CONNECTING DRIVEWORKSEZ (LOWER) | 392 | 1 | 16